{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":38,"n_cols":14,"rows_kept":38,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERAD-E-SS"]
[]
[]
[]
[]
["","","","","ERAD120E-SS","ERAD140E-SS","ERAD170E-SS","ERAD200E-SS","ERAD220E-SS","ERAD250E-SS","ERAD310E-SS","ERAD370E-SS","ERAD440E-SS","ERAD490E-SS"]
["Sound pressure level","Cooling","Nom.","dBA","74 (2)","74 (2)","74 (2)","74 (2)","74 (2)","75 (2)","75 (2)","75 (2)","75 (2)","76 (2)"]
["Refrigerant","Circuits","Quantity","","1","1","1","1","1","1","1","1","1","1"]
["","GWP","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Type","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["Cooling capacity","Nom.","","kW","121 (1)","144 (1)","165 (1)","196 (1)","219 (1)","251 (1)","309 (1)","370 (1)","435 (1)","488 (1)"]
["Power input","Cooling","Nom.","kW","42.1 (1)","51.2 (1)","57.7 (1)","65.6 (1)","74.2 (1)","77.0 (1)","93.8 (1)","123 (1)","148 (1)","161 (1)"]
["Sound power level","Cooling","Nom.","dBA","92","92","92","92","93","94","94","95","95","95"]
["Dimensions","Unit","Width","mm","1,292","1,292","1,292","1,292","1,292","1,292","2,236","2,236","2,236","2,236"]
["","","Depth","mm","2,165","2,165","3,065","3,065","3,965","3,965","3,070","3,070","3,070","3,070"]
["","","Height","mm","2,273","2,273","2,273","2,273","2,273","2,273","2,223","2,223","2,223","2,223"]
["Compressor","Type","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","1","1","1","1","1","1","1","1","1","1"]
["Capacity control","Minimum capacity","","%","25.0","25.0","25.0","25.0","25.0","25.0","25.0","25.0","25.0","25.0"]
["","Method","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Weight","Operation weight","","kg","1,617","1,617","1,781","1,781","1,981","1,981","2,756","2,756","2,756","2,756"]
["","Unit","","kg","1,584","1,584","1,741","1,741","1,936","1,936","2,679","2,679","2,679","2,679"]
["Air heat exchanger","Type","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler"]
["EER","","","","2.88 (1)","2.82 (1)","2.86 (1)","2.99 (1)","2.95 (1)","3.27 (1)","3.30 (1)","3.02 (1)","2.95 (1)","3.02 (1)"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation","(1) - Cooling: evaporating temperature 7°C; ambient air temperature 35°C; unit at full load operation"]
["","","","","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744","(2) - Sound pressure levels are measured at evaporating temp. 7°C; ambient air temp. 35°C, unit at full load operation; standard: ISO 3744"]
["","","","","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %"]
["","","","","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current","(5) - Nominal current in cooling mode: evaporating temp. 7°C, ambient air temp. 35°C; compressors + fans current"]
["","","","","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water"]
["","","","","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases","(11) - Its functioning relies on fluorinated greenhouse gases"]