{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":75,"n_cols":21,"rows_kept":75,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWD-J-SS"]
[]
[]
[]
[]
["","","","","","EWWD120J-SS","EWWD140J-SS","EWWD150J-SS","EWWD180J-SS","EWWD210J-SS","EWWD250J-SS","EWWD280J-SS","EWWD310J-SS","EWWD330J-SS","EWWD360J-SS","EWWD380J-SS","EWWD400J-SS","EWWD450J-SS","EWWD500J-SS","EWWD530J-SS","EWWD560J-SS"]
["Sound pressure level","Cooling","","Nom.","dBA","79.0","79.0","79.0","79.0","79.0","79.0","79.0","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)","82 (3)"]
["Refrigerant","Circuits","","Quantity","","","","","","","","","2","2","2","2","2","2","2","2","2"]
["","GWP","","","","","","","","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Type","","","","","","","","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["Operation range","Condenser","Cooling","Min.","°CDB","","","","","","","","23","23","23","23","23","23","23","23","23"]
["","","","Max.","°CDB","","","","","","","","60","60","60","60","60","60","60","60","60"]
["","Evaporator","Cooling","Min.","°CDB","","","","","","","","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","","","","","","","","15","15","15","15","15","15","15","15","15"]
["Cooling capacity","Nom.","","","kW","119.7","145.7","154.3","177.3","207.3","255.3","284.1","309 (1)","333 (1)","356 (1)","385 (1)","415 (1)","463 (1)","512 (1)","540 (1)","568 (1)"]
["Power input","Cooling","","Nom.","kW","","","","","","","","78.8 (1)","84.6 (1)","90.3 (1)","101 (1)","101 (1)","110 (1)","120 (1)","130 (1)","140 (1)"]
["","Heating","","Nom.","kW","","","","","","","","78.8 (2)","84.6 (2)","90.3 (2)","101 (2)","101 (2)","110 (2)","120 (2)","130 (2)","140 (2)"]
["Sound power level","Cooling","","Nom.","dBA","89.0","89.0","89.0","89.0","89.0","89.0","89.0","94","94","94","94","94","94","94","94","94"]
["COP","","","","","","","","","","","","4.92 (2)","4.94 (2)","4.94 (2)","4.82 (2)","5.12 (2)","5.20 (2)","5.28 (2)","5.16 (2)","5.05 (2)"]
["Refrigerant charge","Per circuit","","","kg","","","","","","","","33.0","33.5","34.0","35.0","36.0","37.0","38.0","38.0","38.0"]
["Dimensions","Unit","","Width","mm","913","913","913","913","913","913","913","913","913","913","913","913","913","913","913","913"]
["","","","Depth","mm","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","","Height","mm","1,020","1,020","1,020","1,020","1,020","1,020","1,020","2,000","2,000","2,000","2,000","2,000","2,000","2,000","2,000","2,000"]
["Compressor","Type","","","","","","","","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Quantity","","","","","","","","","","","2","2","2","2","2","2","2","2","2"]
["Water heat exchanger - condenser","Type","","","","","","","","","","","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube","Single pass shell and tube"]
["","Water flow rate","","Nom.","l/s","","","","","","","","9.3","9.3","10.7","11.0","12.4","12.4","15.2","15.3","17.0"]
["Capacity control","Minimum capacity","","","%","25","25","25","25","25","25","25","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Weight","Operation weight","","","kg","1,211","1,276","1,378","1,415","1,473","1,663","1,675","2,755","2,792","2,830","2,888","2,946","3,136","3,327","3,338","3,350"]
["","Unit","","","kg","1,177","1,233","1,334","1,366","1,416","1,600","1,607","2,668","2,700","2,732","2,782","2,832","3,016","3,200","3,207","3,215"]
["Space heating","Average climate water outlet 35°C","General","SCOP","","","","","","","","","4.04"]
["Water heat exchanger - evaporator","Water flow rate","","Nom.","l/s","","","","","","","","14.8","15.9","17.0","18.4","19.8","22.1","24.5","25.8","27.2"]
["","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water volume","","","l","14","18","14","17","20","26","26","29","31","33","37","41","46","52","52","52"]
["","Water pressure drop","Cooling","Nom.","kPa","15","14","43","40","35","28","34"]
["EER","","","","","4.28","4.28","3.91","3.92","4.11","4.26","4.06","3.92 (1)","3.94 (1)","3.94 (1)","3.82 (1)","4.12 (1)","4.20 (1)","4.28 (1)","4.16 (1)","4.05 (1)"]
["ESEER","","","","","","","","","","","","4.32","4.35","4.50","4.31","4.65","4.74","4.83","4.73","4.33"]
["Heating capacity","Nom.","","","kW","","","","","","","","388 (2)","417 (2)","446 (2)","486 (2)","515 (2)","573 (2)","631 (2)","669 (2)","709 (2)"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Voltage range","","Max.","%","10","10","10","10","10","10","10"]
["","","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Unit","Max unit current for wires sizing","","","A","95","114","127","144","172","197","223"]
["","Starting current","","Max","A","153.0","153.0","197.0","197.0","197.0","290.0","290.0"]
["Notes","","","","","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation."]
["","","","","","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation","(2) - Heating capacity, unit power input and COP are based on the following conditions: evaporator 15/10°C; condensor 40/45°C, unit at full load operation"]
["","","","","","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(3) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(4) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load","(5) - Maximum starting current: starting current of biggest compressor + current of the other compressor at 75 % of maximum load"]
["","","","","","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current","(6) - Nominal current cooling mode is referred to the following conditions: evaporator 12/7°C; condenser 30/35°C; compressors current"]
["","","","","","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope","(7) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","","","","","","","","","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(8) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","","","","","","","","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1","(9) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","","","","","","","","","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water"]
["","","","","","","","","","","","","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(11) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","","","","","","","","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(12) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["Power input","Cooling","","Nom.","kW","28","34","39.5","45.3","50.4","59.9","70"]
["IPLV","","","","","5.18","5.06","5.06","5.05","5.16","5.7","4.88"]
["SEER","","","","","3.89","4.74","3.58","4.59","4.81","5.09","4.42"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Compressor","Quantity","","","","1","1","1","1","1","1","1"]
["","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Starting method","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Operation range","Water side","Evaporator","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","15","15","15","15","15","15","15"]
["Refrigerant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP","","","","1,430.0","1,430.0","1,430.0","1,430.0","1,430.0","1,430.0","1,430.0"]
["","Charge","","","kg","18","35","34","37","37","38","38"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Unit","Running current","Cooling","Nom.","A","48","57","67","74","83","97","109"]
["","","","Max","A","85","103","114","130","154","178","201"]